- Friday, March 11th:

- Earthquake tears through the seafloor off the coast of Honshu Island and Reactor 1, 2, 3 are automatically shut down.

- The power of the power plant got cut off from the national grid and backup diesel generators was started up.

- Tsunami strikes the 19 foot (5.7 meter) high sea wall resulting in shutdown of the diesel generators.

The government issues an emergency evacuation order to all residents within two miles (3km) of the plant.

- Saturday, March 12th:

- Reactor 1 and 2 were vented out to avoid explosion.

.

- Seawater was directly pumped into reactor no.1 in an attempt to keep the core cool.

- The evacuation zone was extended to 12.4 miles (20 km).

- March 14th/15th: Explosion in reactor number 3 causing damage to the cooling system of reactor no.2

- March 16th/17th: Water was transported at the place to control the fuel rods.

Event sequence following earthquake (timing from it: 14:46, 11 March)

|  | Unit 1 | Unit 2 | Unit 3 |
| --- | --- | --- | --- |
| Loss of AC power | + 51 min | + 54 min | + 52 min |
| Loss of cooling | + 1 hour | + 70 hours | + 36 hours |
| Water level down to top of fuel* | + 3 hours | + 74 hours | + 42 hours |
| Core damage starts* | + 4 hours | + 77 hours | + 44 hours |
| Reactor pressure vessel damage* | +11 hours | uncertain | uncertain |
| Fire pumps with fresh water | + 15 hours |  | + 43 hours |
| Hydrogen explosion (not confirmed for unit 2) | + 25 hours service floor | + 87 hours suppression chamber | + 68 hours service floor |
| Fire pumps with seawater | + 28 hours | + 77 hours | + 46 hours |
| Offsite electrical supply | + 11-15 days |  |  |
| Fresh water cooling | + 14-15 days |  |  |